# 6742R	RESENE FIREPROOFING COATINGS - STEELWORK

## 1.	GENERAL

If you have pre-customised this work section using the "questions and answers" provided as part of the downloading process, it may be necessary to amend some clauses to suit the final project-specific version.

The section must still be checked and customised to suit the project being specified, by removing any other irrelevant details and adding project-specific details and selections.

This section relates to the preparation and painting of Resene Paints Ltd / Altex Coatings Ltd intumescent and fireproofing coating systems providing fire rating protection for steelwork.

It includes:

-	exterior and interior structural and miscellaneous steelwork items

Modify expand this clause to suit requirements of this specification section.

Resene Paints Ltd & Altex Coatings Ltd have a large range of fireproofing coating systems for structural and miscellaneous steelwork; only limited ranges are covered in this section.

Resene recommends that a specifier contact the Resene Technical Helpline on 0800 737 363, to ensure the specified coating selection is correct for each particular surface and suitable for the project conditions and exposure.  Furthermore Resene recommends the specifier get advice on the finish coat for each intumescent coating system due to the selection being very project specific.

NOTE: Resene provides a Specification Request Form on the Resene website www.resene.co.nz

### 1.1	RELATED WORK

Refer to 3411 STRUCTURAL STEELWORK for fabrication of structural steelwork.

Include cross references only to other work sections where they include directly related work.

Refer to 6745R RESENE PROTECTIVE COATINGS - STEELWORK for non fire rated finishes.

### 1.2	ABBREVIATIONS AND DEFINITIONS

Refer to the general section 1232 INTERPRETATION & DEFINITIONS for abbreviations and definitions used throughout the specification.

The following abbreviations apply specifically to this section:

DFT	Dry Film Thickness

FRR	Fire Resistance Rating

MPNZA	Master Painters New Zealand Association Inc

Documents

### 1.3	DOCUMENTS

Refer to the general section 1233 REFERENCED DOCUMENTS.  The following documents are specifically referred to in this section:

BS 476.21	Fire tests on buildings and structures - Method for determination of the fire resistance of load bearing elements of construction

AS1530.4	Methods for fire tests on building materials, components and structures - Fire resistance test of elements of construction

AS 1627.4	Metal finishing - Preparation and pretreatment of surfaces - Method selection guide - Abrasive blast cleaning

AS/NZS 2312.1	Guide to the protection of structural steel against atmospheric corrosion by the use of protective coatings - Part 1: Paint coatings

AS/NZS 3750.13	Paints for steel structures - Epoxy primer (2-pack)

AS/NZS ISO 9001	Quality management systems - Requirements

WorkSafe NZ	Guidelines for the provision of facilities and general safety in the construction industry

MPNZA	Health and Safety Program

Delete from the DOCUMENTS clause any document not cited.  List any additional cited documents.

The following are related documents and if referred to in the work section need to be added to the list of DOCUMENTS.

AS/NZS 2311	Guide to the painting of buildings

AS/NZS 3750	Paints for steel structures

AS 3894	Site testing of protective coatings

BS 5493	Protective coating of iron and steel structures against corrosion

Health and Safety in Employment Act 1992

Dangerous Goods Regulations, Flammable Liquids 1985

New Zealand Painting Contractors Association (Inc): Specification manual

### 1.4	MANUFACTURER / SUPPLIER DOCUMENTS

Manufacturer's and supplier's documents relating to this part of the work:

Resene / Altex Coatings / Carboline® Product Data Sheets

Resene / Altex Coatings / Carboline® Safety Data Sheets

List documents relating to this part of the work, i.e. technical product/system specifications, test reports, appraisals, certification, etc. Normally they will be referred to in the text by the abbreviated title.

Manufacturer/supplier contact details

Company:	Resene Paints Ltd

Web:	www.resene.co.nz

Email:	advice@resene.co.nz

Telephone:	0800 737 363 / 04 577 0500

It is important to ensure that all personnel on site have access to accurate, up to date technical information on the many products, materials and equipment used on a project.  In most cases individual products are not used in isolation, but form part of a building process.  Also a particular manufacturer's and/or supplier's requirements for handling, storage, preparation, installation, finishing and protection of their product can vary from what might be considered the norm.  Access to technical information can help overcome this potential problem.

Warranties

### 1.5	WARRANTY

Warrant this work under normal environmental and use conditions against failure of materials and execution.

Product warranty:	Products must be applied in accordance with application and preparation procedures as specified in AS/NZS 2312.1, Resene Paints Ltd specification and product data sheets.  System specified will reflect warranty period.

Refer to the general section for the required form of 1237WA WARRANTY AGREEMENT and details of when completed warranty must be submitted.

Check general section 1237 WARRANTIES for the date of commencement of warranties; which is normally practical completion of the contract.  Refer to the chosen conditions of contract as it may also contain information on warranties/guarantees.

Requirements

### 1.6	QUALIFICATIONS

Painters to be experienced, competent trades people familiar with the materials and techniques specified.

### 1.7	NO SUBSTITUTIONS

Substitutions are not permitted to any of the specified Resene or Altex Coatings  Systems, components and associated products listed in this section without the express written approval from Altex Coatings Technical Services.

### 1.8	SAMPLES

Refer to the general section 1270 CONSTRUCTION for details of how samples will be reviewed and how instructions to proceed will be given.  Provide the following samples for review:

|  | Sample A | Sample B | Sample C |
| --- | --- | --- | --- |
| Sample description: | ~ | ~ | ~ |
| Sample type: | ~ | ~ | ~ |
| Number: | ~ | ~ | ~ |
| Location: | ~ | ~ | ~ |
| Supporting documentation: | ~ | ~ | ~ |
| Reviewer: | Contract administrator ~ | Contract administrator ~ | Contract administrator ~ |
| Time for review: | 10 working days ~ | 10 working days ~ | 10 working days ~ |
| Review criteria: | ~ | ~ | ~ |

The intention of this clause is to allow samples to be obtained that are not otherwise readily available to a reviewer.

Delete rows and columns not required or add "n/a".

| Sample description: | Describe the sample, size etc. Prepare samples of the finished work including the preparation as specified in 3411 STRUCTURAL STEELWORK section. |
| --- | --- |
| Sample type: | Portable sample for review Portable control sample Fixed sample for review Fixed control sample Control samples define requirements for type and quality and are used for comparison purposes throughout the contract. A "portable" sample is a sample that is easily movable, convenient for carrying. A "fixed" sample is a sample (semi) permanently placed. Expand on these terms as necessary. |
| Number: | State number of samples required, e.g. a minimum of three control samples - portable allow a sample to be retained on site with the other samples retained by the contract administrator and contractor. |
| Location: | Identify location of fixed samples, e.g. off site, on site, in situ |
| Supporting documentation: | Describe any additional documents required to support the review. |
| Reviewer: | Modify to suit the project, add additional reviewers if required. |
| Time for review: | Alter time if required. Expand to state timing in relation to when and where the sample is provided, e.g. at first site meeting. |
| Review criteria: | For example: - Appearance - Texture - Colour Add any critical items. Provide clarity for work that is not dependent on the review to continue. |

### 1.9	PRODUCER STATEMENT

Contact Resene Paints Ltd before the shop or on-site application of fireproofing for technical assistance when a manufacturer's producer statement is required.

Performance

### 1.10	QUALITY ASSURANCE

Maintain quality assurance programs to AS/NZS ISO 9001 for both preparation and painting/coating, as necessary to ensure that work is performed in accordance with this specification and the qualifying requirements of the contract documents.

### 1.11	NON CONFORMANCE TO SPECIFICATIONS

Any reduced passive fire protection system performance which may result from the steel preparation and / or selection of specified coatings not being followed in accordance with the specification is outside the control of Resene Paints Ltd.

### 1.12	GENERAL INSPECTIONS

Independent inspection of the work is to take place at each of the stages as scheduled.  Refer to SELECTIONS.  Confirm a written program to facilitate these inspections by an Independent Inspector, including notification when each stage of the work is ready for inspection.

### 1.13	MANUFACTURER'S INSPECTIONS

Permit the paint manufacturer to inspect the work in progress and to take samples of their products from site as requested.  This is not deemed independent inspection but supplier site assistance to help with advice and guidance only.

### 1.14	HEALTH AND SAFETY

Refer to the requirements of the Health and Safety in Employment Act and WorkSafe NZ: Guidelines for the provision of facilities and general safety in the construction industry.  If the elimination or isolation of potential hazards is not possible then minimize hazards in this work on site by using the proper equipment and techniques as set out in the MPNZA Health and Safety Program.  Supply protective clothing and equipment.  Inform employees and others on site of the hazards and put in place procedures for dealing with emergencies.

### 1.15	SAFETY DATA SHEETS

Obtain from Resene Paints Ltd & Altex Coatings Ltd the safety data sheet for each paint product used and comply with the required safety procedures.  Keep sheets in application shop and on site.

Conditions

### 1.16	CONDITIONS - MATERIALS

Use only Resene Paints Ltd & Altex Coatings Ltd products which are guaranteed for consistency and performance under AS/NZS ISO 9001 and when prepared, mixed and applied as directed in the Resene Engineered Coatings Systems & Altex Coatings Ltd Coatings Manual or refer to www.resene.co.nz, www.altexcoatings.co.nz.

## 2.	PRODUCTS

Fireproofing coatings

Where additional information on selected materials and finishing products is necessary include it here.  Otherwise include all relevant information under SELECTIONS.

### 2.1	CEMENTITIOUS FIREPROOFING COATING

Southwest™ Type 5GP, a cementitious, non-combustible, inorganic fireproofing product, tested to AS 1530.4 and BS 476.21.  Available as a spray-on, single component powder mixed with clean water providing a 30 to 240 minute fire rating for interior structural beams, columns and hollow sections.  Refer to SELECTIONS.

Can also be used on steel joists, decks, walls, roofs, girders, floors and precast units.

### 2.2	THIN FILM INTUMESCENT COATING

Firetex® FX2003, solvent based single component, fast drying intumescent coatings, tested to BS 476.21.  Applied by airless-spray, it provides fire protection of interior steel against structural failure for up to 120 minutes.  Refer to SELECTIONS.

### 2.3	THIN FILM WATER-BASED INTUMESCENT COATINGS

Nullifire® S800 Series single component fast drying water-based intumescent coatings tested to BS 476.21.  Applied by airless-spray, they provide fire protection of interior steel against structural failure for up to 120 minutes. Refer to SELECTIONS.

### 2.4	THIN FILM HYBRID INTUMESCENT COATING

Nullifire® SC902, a fast track two-component intumescent capable of being applied as a thin film up to high film thicknesses in a single coat application.  Applied by airless spray it provides fire protection of interior and exterior steel against structural failure for up to 120 minutes.   Refer to SELECTIONS.

Primers

### 2.5	HIGH BUILD ALKYD PRIMER

Rust Arrest or Armourcote 210, both being a modified alkyd zinc phosphate primer, used as a corrosion inhibitor for interior steelwork.  Complies with AS 4089.  Applied by brush, roller or spray.  Refer to SELECTIONS.

### 2.6	GP EPOXY PRIMER

Resene Paints Armourcote 220 and Armourcote 221 or CarboGuard 504, are high performance inhibitive barrier chemically cured epoxy primer.  Complies with AS/NZS 3750.13.  May be applied over mild steel for interior and exterior use.  Refer to SELECTIONS.

Can also be used on non-ferrous metals as well as most GRP substrates.

### 2.7	EPOXY ZINC RICH PRIMER

ArmourZinc 120 and ArmourZinc 125 are two component, high solids, zinc rich epoxy primers for the protection of steel surfaces, where high corrosion resistance is required.  Applied by conventional or airless spray methods.  Refer to SELECTIONS.

Sealers

### 2.8	INTUMESCENT SEALER COAT

Pro-Seal® Intumescent Seal Coat, a single pack solvent based coating used as a seal coat over Firetex FX2003 Intumescent base coat to provide protection from weather, rain and moisture as well as seal the intumescent prior to applying polyurethane finish coats. Also used to promote the cure of Firetex FX2003 to achieve a Shore D50 level of hardness before finish coating. Refer to SELECTIONS

Polyurethanes

### 2.9	POLYURETHANE GLOSS / SEMI-GLOSS / LOW SHEEN FINISH - SOLVENT BASED

Uracryl 400 Series aliphatic acrylic urethane finish for interior and exterior suitably primed structural steel.  Available in a range of colours and gloss levels.  Refer to SELECTIONS.

Isocyanate Free

### 2.10	ISOCYANATE FREE ACRYLIC EPOXY GLOSS / SEMI-GLOSS FINISH - SOLVENT BASED

Imperite IF 503 epoxy reactive acrylic finish for interior and exterior suitably primed structural steel.  Available in a range of colours and gloss levels.  Refer to SELECTIONS.

Water Based Enamels

### 2.11	WATER BASED ACRYLIC ENAMEL GLOSS / SEMI-GLOSS FINISH - WATER BASED

Enamacryl (Gloss) or Lustacryl (semi -gloss) new generation acrylic finish for interior and exterior suitably primed structural steel.  Available in a range of colours and gloss levels.  Refer to SELECTIONS.

Designed for uses where good gloss and colour retention is required.  Also recommended for use on suitably primed aluminium, masonry and fibreglass substrates, and marine applications on above water areas.

Coating systems

### 2.12	COATING SYSTEMS

Refer to SELECTIONS for type.

Where additional information on selected materials and finishing products is necessary include it here.  Otherwise include all relevant information under SELECTIONS.

## 3.	EXECUTION

Conditions

### 3.1	CONDITIONS FOR PAINTING

Coat steelwork in conditions approved for the application of the specified coatings.  Carry out off-site preparation and coating application under cover, in a suitable environment, with adequate lighting and with the air and steel temperature between 10°C and 25°C.

Ensure prepared and painted surfaces are clean and dry.  Do not carry out preparation or painting when the ambient relative humidity exceeds 85%, or when the steel surface temperature is within 3°C of the dew point.

### 3.2	COATING APPLICATION

Apply coatings strictly in accordance with the manufacturer's stated requirements.  Ensure that the manufacturer's latest product data sheets are available for reference during preparation and painting.

### 3.3	COMPATIBILITY

Ensure that materials used and systems applied are approved by the manufacturer for the particular surface and conditions of exposure, and that materials used within each painting system are compatible with each other and are from the same manufacturer group.

### 3.4	SEQUENCE OF OPERATIONS

Complete surface preparation before commencing painting.  Apply paint in the specified sequence using the specified paint.  Allow full drying time between coats to the manufacturer's stated requirements.  Do not expose primers, undercoats and intermediate coats beyond a few days before applying the next coat.

### 3.5	DRYING TIME

Before handling or applying the next coat of paint, give each coat the required drying time required by the manufacturer.

Where high film builds of intumescent are required, apply in thinner multiple coats.  Ensure that surfaces being painted are clean, dry and that ambient conditions are such that condensation does not occur before the paint reaches surface-dry condition.

Multiple thinner coats should be applied in the cooler months of the year, to ensure that not only specified dry film thickness is achieved, but also the complete evacuation of solvents from the film.  This will give each coat a chance to gain sufficient hardness so as not to suffer undue handling damage in-shop or during transport to site.

Application - surface preparation

### 3.6	UNPAINTED SURFACES

Do not paint:

-	Faying face of high strength friction grip (HSFG) bolted joints

-	Areas for site welding keeping 75mm clear all round

### 3.7	SURFACE PREPARATION

Remove all slag.
Ensure that all cut edges are ground to a smooth 2mm radius.

The following applies:

| For welds exposed to view: | Remove weld splatter and grind to a neat, clean finish |
| --- | --- |
| For intumescent fireproofing coating: | Remove rust and mill scale by abrasive blasting to SSPC SP10 (AS1627.4 Class 2½) |

Pre-clean steelwork to SSPC SP1 (AS 1627.1), then carry out abrasive blasting or power tool preparation after completion of the fabrication.  Apply required coating to the coating manufacturer's requirements.  Apply primer coat within 4 hours of preparation. Work off site wherever possible. Surfaces that are in contact or near contact are to receive specified coating before assembly.

Note: some fire protection requires less aggresive preparation, check with manufacturer.

### 3.8	CONDITIONS FOR PREPARING STEELWORK BEING PAINTING

Prepare steelwork in conditions approved for the application of coatings.  Carry out off site preparation and coating applications under cover, in a controlled environment and with adequate lighting.

Delete these clauses when this preparatory work is to be carried out on site by the painter.  Amend also when decorative or protective finishes are covered elsewhere, such as in PAINTING sections.

### 3.9	POWER TOOL CLEANING

Remove oil and grease by the use of solvents.  Scrape and power disc prepare to Class St3 standard in accordance with AS 1627.2 (SSPC SP3) and avoid producing a polished surface.  Check that no burrs or sharp arrises remain which may prevent full coating thickness to be attained.

Delete this clause if the following abrasive blasting clause is used.

Used for non aesthetic/concealed interior steelwork.

### 3.10	ABRASIVE BLASTING

Remove oil and grease by the use of solvents.  Abrasive blast clean to Class 2½ finish to AS 1627.4 (SSPC SP10) and achieve a blast profile between 25 - 50 microns.  Clean to bright metal, but avoid producing a polished surface.  Select a suitable blast media type and equipment such that the cleaned surface profile between peaks and valleys does not exceed one third of the dry film thickness.  Check that no burrs or sharp arrises remain which may prevent the full coating thickness being attained.

Solvent cleaning will not remove chlorides.

Most commonly used for exposed interior steelwork and exterior steelwork.

### 3.11	PREPARING GALVANIZED SURFACES FOR DUPLEX COATING

Round all cut edges to a smooth 2mm radius prior to galvanizing.

Do not dichromate quench as part of galvanizing process prior to duplex coating.  Remove grease, oil and other solvent-soluble contaminants by solvent wiping with D30 Degreaser/Dewaxer.  Allow to dry and proceed with the next operation immediately.  Abrade galvanized surfaces via controlled sweep blasting or abrading to a matt finish.

Contact the manufacturer if unsure of this process.

### 3.12	PREPARING ZINC PRIMED SURFACES

Zinc primers must be free from zinc salts, remove if present.  Remove grease, oil and other solvent-soluble contaminants by solvent wiping with Altex D30 Degreaser/Dewaxer.  Allow to dry and proceed with the next operation immediately.

Application - general

### 3.13	EACH COAT

Each coat of paint and completed paint system to have the following qualities and properties:

-	Uniform finish, colour, texture, sheen and hiding power

-	Correct number of coats applied and DFT achieved

-	Free of defects such as pin holing, alligatoring, blistering, staining, overspray, peeling, runs, sags and wrinkling.

If an architectural finish is intended include in this section a requirement to lightly abrade each coat and state that a high quality architectural finish is to be achieved.

### 3.14	PAINT FILM THICKNESS

The film thickness and dry film thicknesses quoted are the minimum to be achieved. Do not exceed these thicknesses by more than 20% of that specified. The specified film thickness for each coat / application shall be achieved prior to the application of the subsequent coat. Measurement shall be as per AS/NZS 3894.3 standard (SSPC-PA2) and agreed on before commencement of paint application.

### 3.15	PRIMING -GENERALLY

Coat steelwork, unless specifically noted otherwise with the specified priming paint, including patch priming on site after erection.

### 3.16	SHOP PRIMING

Carefully prepare the surface and apply a coat of primer.  Refer to SELECTIONS for dry film build.

Generally use high build primers to give a single coat thickness of between 50 microns and 75 microns.  Use primers that suit the standard of preparation.  Better primers will require abrasive blasted surfaces rather than power tool cleaning.  Ensure suitable, compatible undercoats and top coats are specified elsewhere.  Also check the manufacturer's literature.

There may also be a need to cover the situation where steelwork might be left exposed to the weather for a protracted period.  Other special considerations include suitability of the selected primer under fireproofing materials or coatings.

### 3.17	PATCH PRIMING

Clean and prepare areas of damaged priming and areas left clear for site jointing to a standard comparable with the shop cleaning specified.  Degrease to remove chemical fume deposits resulting from welding as well other contamination.  Apply priming coat/s to same standard as shop primers, ensuring thorough coating of bolts, nuts and connection areas.  Re-prime if the primer fails, or more than 4 weeks lapse before the final coating system is applied.

### 3.18	SITE APPLICATION

Prepare and coat surfaces in conditions approved for the application of coatings.  Prepare primer for intermediate coats by ensuring surfaces are clean and dry.  Lightly abrade primer coat to provide a key.  Apply intermediate coat/s to coating manufacturer's requirements.  Apply final coat to manufacturer's requirements. If the on-site application of intermediate and/or finish coats is via brush/roller multiple coats may be required to achieve the nominated dry film thickness.

Amend if shop application is required.

Amend paint system selection information to include two finish coats if topcoat application is on-site and will be via roller and/or brush.

Important Note: Colours of LRV 25 and below are deemed to be dark and could be problematic. This also applies to interior steel  exposed to sunlight such as atrium locations. Check with Resene or AltexTechnical for further clarification.

### 3.19	SITE REPAIR METALLIC / MIOX FINISHES

Spray application (conventional or HVLP) on site is recommended for repair and touch up of MIOX or Metallic finishes.

### 3.20	BOLTED / WELDED CONNECTIONS AND GALVANIZED BOLTS

Shop applied intumescent coatings which require site welded areas on the primed steel need to be masked off 100mm from welded areas before Intumescent coating is applied.

For fire rated bolted connections allow to apply Intumescent coating at the same DFT of adjacent beam/column, plus finish coat if required.  Contact Altex Coatings Ltd for FR Galvanized Bolt specification.

### 3.21	DRY FILM THICKNESS

Provide the Intumescent DFT specified. If DFT for fire rated sections are not detailed within, contact Resene Paints Ltd / Altex Coatings Ltd for details.

Dry Film Thickness (DFT) of intumescent coating are to be obtained from the Material Spread Sheet issued by Altex Coatings Ltd for each contract.  Note that these DFT's are item specific.

Information required:

FRR requirement i.e. 30 - 120 minutes

Item type - e.g. 350UB46

Item use - beams / columns / bracing

Item length

Number of section sides requiring fire protection

Environment of fire protected steel

### 3.22	WEATHER PROTECTION & OVERCOATING OF INTUMESCENT COATED STEEL SECTIONS

Ensure that the intumescent and Pro-Seal Intumescent Sealer coated sections are hard cured (has achieved Shore D hardness of 50) before being exposed to the weather or top coated (Refer Altex Coatings). Also ensure that the Firetex FX2003 intumescent coated sections are protected against ponding water at all times.
Apply sealer coats to Firetex FX2003 intumescent coated sections if exposure to extended water or extended weather contact is likely to occur (Refer Altex Coatings).

There may also be a need to cover the situation where steelwork might be left exposed to the weather for a protracted period.  Other special considerations include suitability of the selected primer under fireproofing materials or coatings.

### 3.23	PROTECTION OF INTUMESCENT COATED STEEL SECTIONS

Ensure Nullifire® S800 series intumescent coated sections are not exposed to any water, rain or moisture contact (refer to Altex Coatings).

Completion

### 3.24	LEAVE

Leave the whole of this work uniform in gloss, texture and colour, free from painting defects, clean and unmarked, and to the standard required by following procedures.

## 4.	SELECTIONS

For further details on selections go to www.resene.co.nz / www.altexcoatings.co.nz.

Substitutions are not permitted to the following, unless stated otherwise.

If substitutions are permitted modify the statement above, ensure the NO SUBSTITUTIONS clause from GENERAL is treated the same.

Select the options to suit the project and delete options not specified.

Inspections

### 4.1	CONTROL SAMPLES

Manufacturer:	~

Coating system:	~

Nature of sample:	~

### 4.2	GENERAL INSPECTIONS

Coating system:	~

Nature of inspections:	~

New interior concealed structural steel - cementitious sprayed

### 4.3	STRUCTURAL STEEL FRR 30/60/90/120/180/240

(Environmental Classification ISO9223 – C1)

Location:	Dry interior environments only

System:	Cementitious fireproofing

Application:	In-situ only

Preparation:	Degrease as required.  Wire brush to remove loose rust.

1st coat (on site):	Altex Southwest® Type 5GP @ ~ microns DFT

FRR:	~

Options:

1st coat thickness:	Refer to Altex Coatings Ltd for appropriate DFT (depends on FRR required)

FRR:	-/30/30, -/60/60, -/90/90, -/120/120, -180/180, -/240/240

New interior concealed structural steel, hybrid intumescent single-coat system

### 4.4	STRUCTURAL STEEL FRR 30/60/90/120

(Environmental Classification ISO9223 – C1)

Location:	Dry interior environments only

System:	Intumescent

Preparation:	Abrasive blast to AS 1627.4 Class 2½ (SSPC SP10)

1st coat:	Altex Nullifire® SC902 Fast Track Intumescent in accordance with Steel Members Hp/A Value as detailed in the Nullifire loading schedule

1st coat colour:	White

FRR:	~

Options:

1st coat thickness:	Refer to Altex Coatings Ltd for appropriate DFT (depends on FRR required)

FRR:	-/30/30, -/60/60, -/90/90, -/120/120

New interior concealed structural steel, solvent based intumescent

### 4.5	STRUCTURAL STEEL FRR 30/60/90/120 - ALKYD PRIMER + INTUMESCENT

(Environmental Classification ISO9223 – C1 - C2)

Location:	Interior concealed steel

Supplier:	Resene Paints Ltd / Altex Coating Ltd

System:	High Build Alkyd Primer / Intumescent coating

Preparation:	Abrasive blast to AS 1627.4 Class 2½ (SSPC SP10)

1st coat:	Resene Armourcote 210 RA35 @ 75 microns DFT

2nd coat:	Altex Firetex® FX2003 Intumescent in accordance with Steel Members Hp/A Value as detailed in the Firetex loading schedule

3rd coat:	Altex Pro-Seal Intumescent Seal Coat @ 50 microns DFT

3rd coat colour:	~

FRR:	~

Options:

2nd coat thickness:	Refer to Altex Coatings Ltd for appropriate DFT (depends on FRR required)

FRR:	-/30/30, -/60/60

Application of Pro-Seal is specified as it aids in Cure and Weathering Protection:
Where a high end quality finish is sought, it is recommended that an "architectural finish is required" statement is included in this specification.  This will have a direct impact upon the application methodology and cost of the applied system.

### 4.6	STRUCTURAL STEEL, FRR 30/60/90/120 - EPOXY PRIMER + INTUMESCENT

(Environmental Classification ISO9223 – C1 - C2)

Location:	Interior Concealed Steel

Supplier:	Resene Paints Ltd / Altex Coating Ltd

System:	Epoxy Primer / Intumescent coating

Preparation:	Abrasive blast to AS 1627.4 Class 2½; (SSPC SP10)

1st coat:	Altex CarboGuard 635 or CarboGuard 504 @ 75 microns DFT

2nd coat:	Altex Firetex® FX2003 Intumescent in accordance with Steel Members Hp/A Value as detailed in the Firetex loading schedule

3rd coat:	Altex Pro-Seal Intumescent Seal Coat @ 50 microns DFT

3rd coat colour:	~

FRR:	~

Options:

2nd coat thickness:	Refer to Altex Coatings Ltd for appropriate DFT (depends on FRR required)

FRR:	-/30/30, -/60/60

Application of Pro-Seal is specified as it aids in Cure and Weathering Protection:

Where a high end quality finish is sought, it is recommended that an "architectural finish is required" statement is included in this specification.  This will have a direct impact upon the application methodology and cost of the applied system.

New interior concealed structural steel, water-based intumescent

### 4.7	STRUCTURAL STEEL, FRR 30/60/90/120 - INHIBITIVE ALKYD PRIMER + W/B INTUMESCENT

(Environmental Classification ISO9223 – C1 - C2)

Location:	Interior Concealed Steel

System:	High Build Alkyd Primer / Intumescent

Preparation:	Abrasive blast to AS 1627.4 Class 2½ (SSPC SP10)

1st coat:	Resene Armourcote 210 RA35 @ 75 microns DFT. Ensure full cure.

2nd coat:	Altex Nullifire® SC802 Intumescent in accordance with Steel Members Hp/A Value as detailed in the Nullifire loading schedule

2nd coat colour:	White

FRR:	~

Options:

2nd coat thickness:	Refer to Altex Coatings Ltd for appropriate DFT (depends on FRR required)

FRR:	-/30/30, -/60/60, -/90/90, -/120/120

### 4.8	STRUCTURAL STEEL, FRR 30/60/90/120 - EPOXY PRIMER + W/B INTUMESCENT

(Environmental Classification ISO9223 – C1 - C2)

Location:	Interior Concealed Steel

System:	Epoxy Primer / Intumescent

Preparation:	Abrasive blast to AS 1627.4 Class 2½ (SSPC SP10)

1st coat:	Resene Armourcote 220 RA34 @ 75 microns DFT. Ensure full cure.

2nd coat:	AltexNullifire® SC802 Intumescent in accordance with Steel Members Hp/A Value as detailed in the Nullifire loading schedule

2nd coat colour:	White

FRR:	~

Options:

2nd coat thickness:	Refer to Altex Coatings Ltd for appropriate DFT (depends on FRR required)

FRR:	-/30/30, -/60/60, -/90/90, -/120/120

New interior dry visible steel, solvent based intumescent + finish

### 4.9	STRUCTURAL STEEL, FRR 30/60/90/120 – ALKYD PRIMER, SOLVENT BASED URETHANE

(Environmental Classification ISO9223 – C1 - C3)

Location:	Interior Exposed to View

Supplier:	Resene Paints Ltd / Altex Coatings Ltd

System:	Inhibitive Alkyd Primer / Solvent based Intumescent coating / Intumescent Sealer / urethane finish

Preparation:	Abrasive blast to AS 1627.4 Class 2½ (SSPC SP10)

1st coat:	Resene Armourcote 210 RA35 @ 75 microns DFT. Ensure full cure.

2nd coat:	Altex Firetex® FX2003 Intumescent in accordance with Steel Members Hp/A Value as detailed in the Firetex loading schedule

3rd coat:	Altex Pro-Seal Intumescent Seal Coat @ 50 microns DFT

4th colour finish:	Resene Uracryl 400 Series @ 50 microns DFT

5th colour finish:	Resene Uracryl 400 Series @ 50 microns DFT

5th coat finish:	Gloss, Semi-Gloss or Low Sheen

5th coat colour:	~

FRR:	~

Options:

2nd coat thickness:	Refer to Altex Coatings Ltd for appropriate DFT (depends on FRR required)

FRR:	-/30/30, -/60/60, -/90/90, -/120/120

4th & 5th coat colour:	Refer to Resene Paints Ltd for colour range

Important Note: Colours of LRV 25 and below are deemed to be dark and could be problematic if  exposed to direct sunlight such as atrium locations. Check with Resene or AltexTechnical for further clarification.

Where a high end quality finish is sought, it is recommended that an "architectural finish is required" statement is included in this specification.  This will have a direct impact upon the application methodology and cost of the applied system.

### 4.10	STRUCTURAL STEEL, FRR 30/60/90/120 – EPOXY PRIMER, SOLVENT BASED URETHANE

(Environmental Classification ISO9223 – C1 - C3)

Location:	Interior Exposed to View

Supplier:	Resene Paints Ltd / Altex Coatings Ltd

System:	Epoxy Primer / Intumescent coating / Intumescent Sealer / Urethane finish

Preparation:	Abrasive blast to AS 1627.4 Class 2½ (SSPC SP10)

1st coat:	Altex CarboGuard 635 or CarboGuard 504 @ 75 microns DFT

2nd coat:	Altex Firetex® FX2003 Intumescent in accordance with Steel Members Hp/A Value as detailed in the Firetex loading schedule

3rd coat:	Altex Pro-Seal Intumescent Seal Coat @ 50 microns DFT

4th colour finish:	Resene Uracryl 400 Series @ 50 microns DFT

5th colour finish:	Resene Uracryl 400 Series @ 50 microns DFT

5th coat finish:	Gloss, Semi-Gloss or Low Sheen

5th coat colour:	~

FRR:	~

Options:

2nd coat thickness:	Refer to Altex Coatings Ltd for appropriate DFT (depends on FRR required)

FRR:	-/30/30, -/60/60, -/90/90, -/120/120

4th & 5th coat colour:	Refer to Resene Paints Ltd for colour range

Important Note: Colours of LRV 25 and below are deemed to be dark and could be problematic if  exposed to direct sunlight such as atrium locations. Check with Resene or AltexTechnical for further clarification.

Where a high end quality finish is sought, it is recommended that an "architectural finish is required" statement is included in this specification.  This will have a direct impact upon the application methodology and cost of the applied system.

### 4.11	STRUCTURAL STEEL, FRR 30/60/90/120 – SOLVENT BASED, ISOCYANATE FREE, METALLIC GLOSS FINISH

(Environmental Classification ISO9223 – C1 – C3)

Location:	Interior Exposed to View

Supplier:	Resene Paints Ltd / Altex Coatings Ltd

System:	Epoxy Primer / Intumescent coating / intumescent sealer / acrylic epoxy finish

Preparation:	Abrasive blast to AS 1627.4 Class 2½ (SSPC SP10)

1st coat:	Altex CarboGuard 635 or CarboGuard 504 @ 75 microns DFT

2nd coat:	Altex Firetex® FX2003 Intumescent in accordance with Steel Members Hp/A Value as detailed in the Firetex loading schedule

3rd coat:	Altex Pro-Seal Intumescent Seal Coat @ 50 microns DFT

4th colour finish:	Resene Imperite IF503 RA81 @ 50 microns DFT

5th colour finish:	Resene Imperite IF503 RA81 @ 50 microns DFT

6th coat: (optional)	Resene Imperite IF503 Clear Gloss RA81 @ 30 microns DFT

5th coat finish:	Metallic Gloss

5th coat colour:	~

FRR:	~

Options:

2nd coat thickness:	Refer to Altex Coatings Ltd for appropriate DFT (depends on FRR required)

FRR:	-/30/30, -/60/60

4th & 5th coat colour:	Refer to Resene Paints Ltd for colour range

Important Note: Colours of LRV 25 and below are deemed to be dark and could be problematic if  exposed to direct sunlight such as atrium locations. Check with Resene or AltexTechnical for further clarification.

Where a high end quality finish is sought, it is recommended that an "architectural finish is required" statement is included in this specification.  This will have a direct impact upon the application methodology and cost of the applied system.

### 4.12	STRUCTURAL STEEL, FRR 30/60/90/120 – SOLVENT BASED, ISOCYANATE FREE, METALLIC SEMI-GLOSS FINISH

(Environmental Classification ISO9223 – C1 – C3)

Location:	~

Supplier:	Resene Paints Ltd / Altex Coatings Ltd

System:	Epoxy Primer / Intumescent coating / intumescent sealer / acrylic epoxy finish

Preparation:	Abrasive blast to AS 1627.4 Class 2½ (SSPC SP10)

1st coat:	Altex CarboGuard 635 or CarboGuard 504 @ 75 microns DFT

2nd coat:	Altex Firetex® FX2003 Intumescent in accordance with Steel Members Hp/A Value as detailed in the Firetex loading schedule

3rd coat:	Altex Pro-Seal Intumescent Seal Coat @ 50 microns DFT

4th colour finish:	Resene Imperite IF 503 RA81 @ 50 microns DFT

5th clear finish:	Resene Imperite IF 503 RA81 @ 50 microns DFT

6th coat: (optional)	Resene Imperite IF502 Clear Semi-Gloss RA82 @ 30 microns DFT

5th coat finish:	Metallic Semi-Gloss

5th coat colour:	~

FRR:	~

Options:

2nd coat thickness:	Refer to Altex Coatings Ltd for appropriate DFT (depends on FRR required)

FRR:	-/30/30, -/60/60

4th & 5th coat colour:	Refer to Resene Paints Ltd for colour range

Important Note: Colours of LRV 25 and below are deemed to be dark and could be problematic if  exposed to direct sunlight such as atrium locations. Check with Resene or AltexTechnical for further clarification.

Where a high end quality finish is sought, it is recommended that an "architectural finish is required" statement is included in this specification.  This will have a direct impact upon the application methodology and cost of the applied system.

New interior visible structural steel, water-based intumescent, urethane finish

### 4.13	STRUCTURAL STEEL, FRR 30/60/90/120 –  INHIBITIVE ALKYD PRIMER, URETHANE FINISH

(Environmental Classification ISO9223 – C1 – C3)

Location:	~

Supplier:	Resene Paints Ltd / Altex Coatings Ltd

System:	Inhibitive alkyd primer /water-based Intumescent / Solvent based urethane (x2)

Preparation:	Abrasive blast to AS 1627.4 Class 2½ (SSPC SP10)

1st coat:	Resene Armourcote 210 RA35 @ 75 microns DFT.

2nd coat:	AltexNullifire® SC800 Series Intumescent in accordance with Steel Members Hp/A Value as detailed in the Nullifire loading schedule

3rd colour finish:	Resene Uracryl 400 Series @ 50 microns DFT (Apply as a tack coat/full coat application by spray)

4th colour finish:	Resene Uracryl 400 Series @ 50 microns DFT

4th coat finish:	Gloss, Semi-Gloss or Low Sheen

4th coat colour:	~

FRR:	~

Options:

2nd coat thickness:	Refer to Altex Coatings Ltd for appropriate DFT (depends on FRR required)

FRR:	-/30/30, -/60/60, -/90/90, -/120/120

3rd & 4th coat colour:	Refer to Resene Paints Ltd for colour range

Important Note: Colours of LRV 25 and below are deemed to be dark and could be problematic if  exposed to direct sunlight such as atrium locations. Check with Resene or AltexTechnical for further clarification.

Where a high end quality finish is sought, it is recommended that an "architectural finish is required" statement is included in this specification.  This will have a direct impact upon the application methodology and cost of the applied system.

### 4.14	STRUCTURAL STEEL, FRR 30/60/90/120 –  EPOXY PRIMER, URETHANE FINISH

(Environmental Classification ISO9223 – C1 – C3)

Location:	~

Supplier:	Resene Paints Ltd / Altex Coatings Ltd

System:	Epoxy Primer /water-based Intumescent / Solvent based urethane (x2)

Preparation:	Abrasive blast to AS 1627.4 Class 2½ (SSPC SP10)

1st coat:	Resene Armourcote 220 RA34 @ 75 microns DFT.

2nd coat:	AltexNullifire® SC800 Series Intumescent in accordance with Steel Members Hp/A Value as detailed in the Nullifire loading schedule

3rd colour finish:	Resene Uracryl 400 Series@ 50 microns DFT (Apply as a tack coat/full coat application by spray)

4th colour finish:	Resene Uracryl 400 Series @ 50 microns DFT

4th coat finish:	Gloss, Semi-Gloss or Low Sheen

4th coat colour:	~

FRR:	~

Options:

2nd coat thickness:	Refer to Altex Coatings Ltd for appropriate DFT (depends on FRR required)

FRR:	-/30/30, -/60/60, -/90/90, -/120/120

3rd & 4th coat colour:	Refer to Resene Paints Ltd for colour range

Important Note: Colours of LRV 25 and below are deemed to be dark and could be problematic if  exposed to direct sunlight such as atrium locations. Check with Resene or AltexTechnical for further clarification.

Where a high end quality finish is sought, it is recommended that an "architectural finish is required" statement is included in this specification.  This will have a direct impact upon the application methodology and cost of the applied system.

New interior visible structural steel, 30 – 120 FRR, waterborne intumescent + water-based enamel finish

### 4.15	STRUCTURAL STEEL, FRR 30/60/90/120 – INHIBITIVE ALKYD PRIMER, WATER-BASED ENAMEL, GLOSS FINISH

(Environmental Classification ISO9223 – C1 – C2)

Location:	~

Supplier:	Resene Paints Ltd / Altex Coatings Ltd

System:	Inhibitive alkyd primer /water-based intumescent coating / water-based enamel

Preparation:	Abrasive blast to AS 1627.4 Class 2½ (SSPC SP10)

1st coat:	Resene Armourcote 210 RA35 @ 75 microns DFT

2nd coat:	Altex Nullifire® SC800 Series Intumescent in accordance with Steel Members Hp/A Value as detailed in the Nullifire loading schedule

3rd colour finish:	Resene Enamacryl D309 @ 35 microns DFT

4th colour finish:	Resene Enamacryl D309 @ 35 microns DFT

4th coat finish:	Gloss

4th coat colour:	~

FRR:	~

Options:

2nd coat thickness:	Refer to Altex Coatings Ltd for appropriate DFT (depends on FRR required)

FRR:	-/30/30, -/60/60, -/90/90, -/120/120

3rd & 4th coat colour:	Refer to Resene Paints Ltd for colour range

Important Note: Colours of LRV 25 and below are deemed to be dark and could be problematic if  exposed to direct sunlight such as atrium locations. Check with Resene or AltexTechnical for further clarification.

Where a high end quality finish is sought, it is recommended that an "architectural finish is required" statement is included in this specification.  This will have a direct impact upon the application methodology and cost of the applied system.

### 4.16	STRUCTURAL STEEL, FRR 30/60/90/120  EPOXY PRIMER, WATER-BASED ENAMEL, GLOSS FINISH

(Environmental Classification ISO9223 – C1 – C2)

Location:	~

Supplier:	Resene Paints Ltd / Altex Coatings Ltd

System:	Epoxy Primer / Intumescent coating / acrylic enamel finish

Preparation:	Abrasive blast to AS 1627.4 Class 2½ (SSPC SP10)

1st coat:	Resene Armourcote 220 RA34 @ 75 microns DFT

2nd coat:	Altex Nullifire® SC800 Series Intumescent in accordance with Steel Members Hp/A Value as detailed in the Nullifire loading schedule

3rd colour finish:	Resene Enamacryl D309 @ 35 microns DFT

4th colour finish:	Resene Enamacryl D309 @ 35 microns DFT

4th coat finish:	Gloss

4th coat colour:	~

FRR:	~

Options:

2nd coat thickness:	Refer to Altex Coatings Ltd for appropriate DFT (depends on FRR required)

FRR:	-/30/30, -/60/60, -/90/90, -/120/120

3rd & 4th coat colour:	Refer to Resene Paints Ltd for colour range

Important Note: Colours of LRV 25 and below are deemed to be dark and could be problematic if  exposed to direct sunlight such as atrium locations. Check with Resene or AltexTechnical for further clarification.

Where a high end quality finish is sought, it is recommended that an "architectural finish is required" statement is included in this specification.  This will have a direct impact upon the application methodology and cost of the applied system.

### 4.17	STRUCTURAL STEEL, FRR 30/60/90/120 – WATER-BASED ENAMEL, SEMI-GLOSS FINISH

(Environmental Classification ISO9223 – C1 - C2)

Location:	~

Supplier:	ResenePaints Ltd / Altex Coatings Ltd

System:	Inhibitive Alkyd Primer / Water-based Intumescent / water-based enamel semi-gloss finish

Preparation:	Abrasive blast to AS 1627.4 Class 2½ (SSPC SP10)

1st coat:	Resene Armourcote 210 RA35 @ 75 microns DFT

2nd coat:	Altex Nullifire® SC800 Series Intumescent in accordance with Steel Members Hp/A Value as detailed in the Nullifire loading schedule

3rd colour finish:	Resene Lustacryl D310 @ 35 microns DFT

4th colour finish:	Resene Lustacryl D310 @ 35 microns DFT

4th coat finish:	Semi-Gloss

4th coat colour:	~

FRR:	~

Options:

2nd coat thickness:	Refer to Altex Coatings Ltd for appropriate DFT (depends on FRR required)

FRR:	-/30/30, -/60/60, -/90/90, -/120/120

3rd & 4th coat colour:	Refer to Resene Paints Ltd for colour range

Important Note: Colours of LRV 25 and below are deemed to be dark and could be problematic if  exposed to direct sunlight such as atrium locations. Check with Resene or AltexTechnical for further clarification.

Where a high end quality finish is sought, it is recommended that an "architectural finish is required" statement is included in this specification.  This will have a direct impact upon the application methodology and cost of the applied system.

### 4.18	STRUCTURAL STEEL, FRR 30/60/90/120 – WATER-BASED ENAMEL, SEMI-GLOSS FINISH

(Environmental Classification ISO9223 – C1 - C2)

Location:	~

Supplier:	Resene Paints Ltd / Altex Coatings Ltd

System:	Epoxy Primer / Intumescent coating / acrylic enamel finish

Preparation:	Abrasive blast to AS 1627.4 Class 2½ (SSPC SP10)

1st coat:	Resene Armourcote 220 RA34 @ 75 microns DFT

2nd coat:	AltexNullifire® SC800 Series Intumescent in accordance with Steel Members Hp/A Value as detailed in the Nullifire loading schedule

3rd colour finish:	Resene Lustacryl D310 @ 35 microns DFT

4th colour finish:	Resene Lustacryl D310 @ 35 microns DFT

4th coat finish:	Semi-Gloss

4th coat colour:	~

FRR:	~

Options:

2nd coat thickness:	Refer to Altex Coatings Ltd for appropriate DFT (depends on FRR required)

FRR:	-/30/30, -/60/60, -/90/90, -/120/120

3rd & 4th coat colour:	Refer to Resene Paints Ltd for colour range

Important Note: Colours of LRV 25 and below are deemed to be dark and could be problematic if  exposed to direct sunlight such as atrium locations. Check with Resene or AltexTechnical for further clarification.

Where a high end quality finish is sought, it is recommended that an "architectural finish is required" statement is included in this specification.  This will have a direct impact upon the application methodology and cost of the applied system.

### 4.19	STRUCTURAL STEEL, FRR 30/60/90/120 – WATER-BASED ENAMEL, LOW SHEEN FINISH

(Environmental Classification ISO9223 – C1 - C2)

Location:	~

Supplier:	Resene Paints Ltd / Altex Coatings Ltd

System:	Inhibitive Alkyd Primer /Water-based Intumescent / water-based enamel low sheen finish

Preparation:	Abrasive blast to AS 1627.4 Class 2½ (SSPC SP10)

1st coat:	Resene Armourcote 210 RA34 @ 75 microns DFT

2nd coat:	Altex Nullifire® SC800 Series Intumescent in accordance with Steel Members Hp/A Value as detailed in the Nullifire loading schedule

3rd colour finish:	Resene Spacecote D311 @ 35 microns DFT

4th colour finish:	Resene Spacecote D311 @ 35 microns DFT

4th coat finish:	Low Sheen

4th coat colour:	~

FRR:	~

Options:

2nd coat thickness:	Refer to Altex Coatings Ltd for appropriate DFT (depends on FRR required)

FRR:	-/30/30, -/60/60, -/90/90, -/120/120

3rd & 4th coat colour:	Refer to Resene Paints Ltd for colour range

Important Note: Colours of LRV 25 and below are deemed to be dark and could be problematic if  exposed to direct sunlight such as atrium locations. Check with Resene or AltexTechnical for further clarification.

Where a high end quality finish is sought, it is recommended that an "architectural finish is required" statement is included in this specification.  This will have a direct impact upon the application methodology and cost of the applied system.

### 4.20	STRUCTURAL STEEL, FRR 30/60/90/120 – WATER-BASED ENAMEL, LOW SHEEN FINISH

(Environmental Classification ISO9223 – C1 - C2)

Location:	~

Supplier:	Resene Paints Ltd / Altex Coatings Ltd

System:	Epoxy Primer  /Water-based Intumescent / water-based enamel low sheen finish

Preparation:	Abrasive blast to AS 1627.4 Class 2½ (SSPC SP10)

1st coat:	Resene Armourcote 220 RA34 @ 75 microns DFT

2nd coat:	Altex Nullifire® SC800 Series Intumescent in accordance with Steel Members Hp/A Value as detailed in the Nullifire loading schedule

3rd colour finish:	Resene Spacecote D311 @ 35 microns DFT

4th colour finish:	Resene Spacecote D311 @ 35 microns DFT

4th coat finish:	Low Sheen

4th coat colour:	~

FRR:	~

Options:

2nd coat thickness:	Refer to Altex Coatings Ltd for appropriate DFT (depends on FRR required)

FRR:	-/30/30, -/60/60, -/90/90, -/120/120

3rd & 4th coat colour:	Refer to Resene Paints Ltd for colour range

Important Note: Colours of LRV 25 and below are deemed to be dark and could be problematic if  exposed to direct sunlight such as atrium locations. Check with Resene or AltexTechnical for further clarification.

Where a high end quality finish is sought, it is recommended that an "architectural finish is required" statement is included in this specification.  This will have a direct impact upon the application methodology and cost of the applied system.

New Exterior Visible Structural Steel, 30 – 120 FRR, solvent based intumescent + finish

### 4.21	STRUCTURAL STEEL, FRR 30/60/90/120 FRR, HIGH PERFORMANCE PROTECTION & FINISH

(Environmental Classification – Maximum of ISO9223 – C1 – C4)

Location:	~

Supplier:	Resene Paints Ltd / Altex Coatings Ltd

System:	Epoxy Zinc Rich / Epoxy Primer / Intumescent / Urethane (x2)

Preparation:	Abrasive blast to AS 1627.4 Class 2½ (SSPC SP10)

1st coat:	Resene Armourzinc 120 RA22 @ 75 microns DFT

2nd coat:	Resene Armourcote 220 RA34 @ 75 microns DFT

3rd coat:	Altex Nullifire® SC902 Intumescent in accordance with Steel Members Hp/A Value as detailed in the Nullifire loading schedule

4th coat:	Resene Imperite IF503 RA81 @ 75 microns DFT

5th coat:	Resene Imperite IF503 RA81 @ 75 microns DFT

5th coat finish:	Gloss

5th coat colour:	~

FRR:	~

Options:

2nd coat thickness:	Refer to Altex Coatings Ltd for appropriate DFT (depends on FRR required)

FRR:	30/30/30, 60/60/60, 90/90/90, 120/120/120

4th & 5th coat colour:	Refer to Resene Paints Ltd for colour range

Important Note: Colours of LRV 25 and below are deemed to be dark and could be problematic if  exposed to direct sunlight such as atrium locations. Check with Resene or AltexTechnical for further clarification.

Where a high end quality finish is sought, it is recommended that an "architectural finish is required" statement is included in this specification.  This will have a direct impact upon the application methodology and cost of the applied system.

New Exterior Visible Hot Dipped Galvanized Steel, 30 – 120 FRR, solvent-based intumescent + finish

### 4.22	NEW EXTERIOR GALVANIZED STEEL, FRR 30/60/90/120 HIGH PERFORMANCE PROTECTION & FINISH

(Environmental Classification – Maximum of ISO9223 – C1 - C4)

Location:	~

Supplier:	Resene Paints Ltd / Altex Coatings Ltd

System:	Epoxy Primer / Intumescent / Urethane

Preparation:	Degrease, sweep abrasive blast

1st coat:	Resene Armourcote 220 RA34 @ 75 microns DFT

2nd coat:	Nullifire® SC902 Intumescent in accordance with Steel Members Hp/A Value as detailed in the Nullifire loading schedule.

3rd coat:	Resene Imperite IF503 RA81 @ 75 microns DFT

4th coat:	Resene Imperite IF503 RA81 @ 75 microns DFT

4th coat finish:	Gloss

4th coat colour:	~

FRR:	~

Options:

2nd coat thickness:	Refer to Altex Coatings Ltd for appropriate DFT (depends on FRR required)

FRR:	30/30/30, 60/60/60, 90/90/90, 120/120/120

3rd & 4th coat colour:	Refer to Resene Paints Ltd for colour range

Important Note: Colours of LRV 25 and below are deemed to be dark and could be problematic. Check with Resene or AltexTechnical for further clarification.

Where a high end quality finish is sought, it is recommended that an "architectural finish is required" statement is included in this specification.  This will have a direct impact upon the application methodology and cost of the applied system.